Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This Product MasterSpec Section is licensed by ARCOM for limited distribution by Legend Valve & Fitting, Inc., ("Licensee").  The license is subject to revocation by ARCOM subject to the Product MasterSpec License Agreement between ARCOM and Licensee.

A clean version (revisions accepted) and an underline-and-strikeout version of this Section, both of which modify the original MasterSpec text, are distributed by Licensee to assist in specifying Licensee's products.   Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, ARCOM or The American Institute of Architects (AIA).  Neither AIA nor ARCOM are liable in any way for such revisions or for the use of this Product MasterSpec Section by Licensee or any end user to which Licensee distributes this Product MasterSpec Section.  A qualified design professional should review and edit the document to suit project requirements.  For more information, contact Legend Valve & Fitting, Inc., 51245 Filomena Drive, Shelby Township, MI 48315; phone:  (800) 752-2082; fax:  (800) 835-4457; Website:  www.legendvalve.com; e-mail:  mike.boehk@legendvalve.com.  For information about MASTERSPEC contact ARCOM at (800) 424-5080 or visit www.arcomnet.com.

SECTION 220523 - GENERAL-DUTY VALVES FOR PLUMBING PIPING

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Bronze angle valves.

Brass ball valves.

Bronze ball valves.

Carbon steel ball valves.

Stainless steel ball valves.

Iron ball valves.

Ductile iron, single-flange butterfly valves.

Ductile iron wafer butterfly valves.

Iron, grooved-end butterfly valves.

Bronze lift check valves.

Bronze swing check valves.

Iron swing check valves.

Iron swing check valves with closure control.

Iron, grooved-end swing check valves.

Iron, center-guided check valves.

Iron, plate-type check valves.

Bronze gate valves.

Iron gate valves.

Bronze globe valves.

Iron globe valves.

Chainwheels.

Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

Division 22 plumbing piping Sections for specialty valves applicable to those Sections only.

Division 22 Section "Identification for Plumbing Piping and Equipment" for valve tags and schedules.

Division 33 water distribution piping Sections for general-duty and specialty valves for site construction piping.

DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

Legend Valve advises the specifier that Buna-N and NBR are the same material (a copolymer of butadiene and acrylonitrile) and that these material designations are used interchangeably.

Buna-N:  Nitrile copolymer of butadiene and acrylonitrile.

CWP:  Cold working pressure.

EPDM:  Ethylene propylene-diene monomer rubber.

MSS:  Manufacturer’s Standardization Society.

NBR:  Acrylonitrile-butadiene, Buna-N, or nitrile rubber.

NRS:  Nonrising stem.

NSF:  National Sanitation Foundation.

OS&Y:  Outside screw and yoke.

PTFE:  Polytetrafluoroethylene.

RPTFE:  Reinforced Polytetrafluoroethylene.

RS:  Rising stem.

SWP:  Steam working pressure.

WOG:  Water, oil and gas.

ACTION SUBMITTALS

Product Data:  For each type of valve indicated.

QUALITY ASSURANCE

Source Limitations for Valves:  Obtain each type of valve from single source from single manufacturer.

ASME Compliance:

ASME B16.10 and ASME B16.34 for ferrous valve dimensions and design criteria.

ASME B31.1 for power piping valves.

ASME B31.9 for building services piping valves.

NSF Compliance:  NSF 61 for valve materials for potable-water service.

DELIVERY, STORAGE, AND HANDLING

Information in this article is paraphrased from MSS.

Prepare valves for shipping as follows:

Protect internal parts against rust and corrosion.

Protect threads, flange faces, grooves, and weld ends.

Set angle, gate, and globe valves closed to prevent rattling.

Set ball and plug valves open to minimize exposure of functional surfaces.

Set butterfly valves closed or slightly open.

Block check valves in either closed or open position.

Use the following precautions during storage:

Maintain valve end protection.

Store valves indoors and maintain at higher than ambient dew point temperature.  If outdoor storage is necessary, store valves off the ground in watertight enclosures.

Use sling to handle large valves; rig sling to avoid damage to exposed parts.  Do not use handwheels or stems as lifting or rigging points.

PRODUCTS

GENERAL REQUIREMENTS FOR VALVES

Plumbing valve applications specified in this Section are limited to NPS 12 (DN 300).  Many valves specified are available in larger sizes.

Refer to valve schedule articles for applications of valves.

Caution:  Revise pressure ratings and insert temperature ratings in valve articles if valves with higher ratings are required.  Valves larger than NPS 12 (DN 300) typically have a lower pressure rating than smaller valves.  Verify pressure requirements for large valves.

Valve Pressure and Temperature Ratings:  Not less than indicated and as required for system pressures and temperatures.

Valve Sizes:  Same as upstream piping unless otherwise indicated.

Valve Actuator Types:

Gear Actuator:  For quarter-turn valves NPS 8 (DN 200) and larger.

Handwheel:  For valves other than quarter-turn types.

Handlever:  For quarter-turn valves NPS 6 (DN 150) and smaller[ except plug valves].

Wrench:  For plug valves with square heads.  Furnish Owner with 1 wrench for every [5] [10] <Insert number> plug valves, for each size square plug-valve head.

Chainwheel:  Device for attachment to valve handwheel, stem, or other actuator; of size and with chain for mounting height, as indicated in the "Valve Installation" Article.

Valves in Insulated Piping:  With 2-inch (50-mm) stem extensions and the following features:

Gate Valves:  With rising stem.

Ball Valves:  With extended operating handle of non-thermal-conductive material, and protective sleeve that allows operation of valve without breaking the vapor seal or disturbing insulation.

Butterfly Valves:  With extended neck.

Valve-End Connections:

Flanged:  With flanges according to ASME B16.1 for iron valves.

Grooved:  With grooves according to AWWA C606.

Valve solder-joint connections are common in smaller sizes of plumbing piping.  Soldering and brazing methods used to achieve required pressure-temperature ratings may damage internal valve parts.  Special installation requirements for soldered valves may make threaded valves more cost-effective.

Caution:  Use solder with melting point below 840 deg F (454 deg C) for angle, check, gate, and globe valves and below 421 deg F (216 deg C) for ball valves.

Solder Joint:  With sockets according to ASME B16.18.

Threaded:  With threads according to ASME B1.20.1.

Valve Bypass and Drain Connections:  MSS SP-45.

BRONZE ANGLE VALVES

Retain one or more of four paragraphs in this article if bronze angle valves are required.  MSS SP-80 covers bronze angle valves NPS 1/4 to NPS 3 (DN 8 to DN 80).

Two-Piece, Full-Port, Brass Ball Valves with Brass Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; [Model S-1001] [Model T-1001], or a comparable product by one of the following:

Description:

Standard:  MSS SP-110.

SWP Rating:  150 psig (1035 kPa).

CWP Rating:  600 psig (4140 kPa).

Body Design:  Two piece.

Body Material:  Forged brass.

Ends:  Threaded or solder.

Seats:  PTFE.

Stem:  Brass.

Ball:  Chrome-plated brass.

Port:  Full.

Two-Piece, Full-Port, Brass Ball Valves with Stainless-Steel Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; [Model T-1002ST] [Model T-1002STLD], or a comparable product by one of the following:

Description:

Standard:  MSS SP-110.

SWP Rating:  150 psig (1035 kPa).

CWP Rating:  600 psig (4140 kPa).

Body Design:  Two piece.

Body Material:  Forged brass.

Ends:  Threaded.

Seats:  PTFE.

Stem:  Stainless steel.

Ball:  Stainless steel.

Port:  Full.

Two-Piece, Regular-Port, Brass Ball Valves with Brass Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; [Model S-800] [Model T-800], or a comparable product by one of the following:

Description:

Standard:  MSS SP-110.

SWP Rating:  150 psig (1035 kPa).

CWP Rating:  600 psig (4140 kPa).

Body Design:  Two piece.

Body Material:  Forged brass.

Ends:  Threaded.

Seats:  PTFE or TFE.

Stem:  Brass.

Ball:  Chrome-plated brass.

Port:  Regular.

Two-Piece, Regular-Port, Brass Ball Valves with Stainless-Steel Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Two-Piece, Full-Port, Bronze Ball Valves with Bronze Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; [Model S-901] [Model T-901], or a comparable product by one of the following:

Conbraco Industries, Inc.; Apollo Valves.

Milwaukee Valve Company.

<Insert manufacturer's name>.

Description:

Standard:  MSS SP-110.

SWP Rating:  150 psig (1035 kPa).

CWP Rating:  600 psig (4140 kPa).

Body Design:  Two piece.

Body Material:  Bronze.

Ends:  Threaded or solder.

Seats:  PTFE.

Stem:  Bronze.

Ball:  Chrome-plated brass.

Port:  Full.

Two-Piece, Full-Port, Bronze Ball Valves with Stainless-Steel Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

CARBON STEEL BALL VALVES

Retain one or more of three paragraphs in this article if carbon steel ball valves are required.  MSS SP-72 covers carbon steel ball valves NPS 1/2 to NPS 36 (DN 15 to DN 900).

Two-Piece, Full-Port Carbon Steel Ball Valves:

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-730, or a comparable product by one of the following:

Description:

Standard:  MSS SP-10.

SWP Rating:  150 psig (1035 kPa).

CWP Rating:  2000 psig (13,800 kPa).

Body Design:  Two-piece.

Body Material:  Carbon steel.

Ends:  Threaded.

Seats:  PTFE.

Stem:  Stainless steel.

Ball:  Stainless steel.

Port:  Full.

Two-Piece, Regular-Port Carbon Steel Ball Valves:

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-725, or a comparable product by one of the following:

Description:

Standard:  MSS SP-10.

SWP Rating:  150 psig (1035 kPa).

CWP Rating:  2000 psig (13,800 kPa).

Body Design:  Two-piece.

Body Material:  Carbon steel.

Ends:  Threaded.

Seats:  RTFE.

Stem:  Stainless steel.

Ball:  Stainless steel.

Port:  Regular or large.

One-Piece, Reduced Port Carbon Steel Barstock Ball Valves:

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-720, or a comparable product by one of the following:

Description:

Standard:  MSS SP-10.

SWP Rating:  150 psig (1035 kPa).

CWP Rating:  2000 psig (13,800 kPa).

Body Design:  One-piece.

Body Material:  Carbon steel barstock.

Ends:  Threaded.

Seats:  PTFE.

Stem:  Stainless steel.

Ball:  Stainless steel.

Port:  Regular.

STAINLESS STEEL BALL VALVES

Retain one or more of four paragraphs in this article if stainless steel ball valves are required.  MSS SP-72 covers stainless steel ball valves NPS 1/2 to NPS 36 (DN 15 to DN 900).

Two-piece, Full-Port Stainless Steel Ball Valves:

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-712, or a comparable product by one of the following:

Description:

Standard:  MSS SP-110.

SWP Rating:  150 psig (1035 kPa).

CWP Rating:  1000 psig (6895 kPa).

Body Design:  Two piece.

Body Material:  Stainless steel.

Ends:  Threaded.

Seats:  PTFE.

Stem:  Stainless steel.

Ball:  Stainless steel.

Port:  Full.

Two-Piece, Large-Port, Stainless Steel Ball Valves:

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-715 or a comparable product by one of the following:

Description:

Standard:  MSS SP-110.

SWP Rating:  150 psig (1035 kPa).

CWP Rating:  2000 psig (800 kPa).

Body Design:  Two piece.

Body Material:  Stainless steel.

Ends:  Threaded.

Seats:   RTFE

Stem:  Stainless steel.

Ball:  Stainless steel.

Port:  Regular or large.

One-Piece, Regular-Port, Stainless Steel Ball Valves:

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-710, or a comparable product by one of the following:

Description:

Standard:  MSS SP-110.

SWP Rating:  150 psig (1035 kPa).

CWP Rating:  800 psig (5515 kPa).

Body Design: One piece.

Body Material:  Stainless steel.

Ends:  Threaded.

Seats:  PTFE.

Stem:  Stainless steel.

Ball:  Stainless steel.

Port:  Regular.

Three-Piece, Full-Port, Stainless Steel Ball Valves:

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-717, or a comparable product by one of the following:

Description:

Standard:  MSS SP-110.

SWP Rating:  150 psig (1035 kPa).

CWP Rating:  1000 psig (6895 kPa).

Body Design: Three-piece.

Body Material:  Stainless steel.

Ends:  Threaded.

Seats:  PTFE.

Stem:  Stainless steel.

Ball:  Stainless steel.

Bolts:  Stainless steel.

Port:  Full.

IRON BALL VALVES

Retain this article if iron ball valves are required.  MSS SP-72 covers iron ball valves NPS 1/2 to NPS 36 (DN 15 to DN 900).

Class 125, Iron Ball Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

DUCTILE IRON, SINGLE-FLANGE BUTTERFLY VALVES

Retain one or more of six paragraphs in this article if iron, single-flange butterfly valves are required.  MSS SP-67 covers iron, single-flange butterfly valves NPS 1-1/2 to NPS 72 (DN 40 to DN 1800).

200 CWP, Ductile Iron, Single-Flange Butterfly Valves with EPDM Seat and Aluminum-Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-365AB, or a comparable product by one of the following:

Description:

Standard:  MSS SP-67, Type I.

CWP Rating:  200 psig (1380 kPa).

Body Design:  Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

Body Material:  ASTM A 536, ductile iron.

Seat:  EPDM.

Stem:  One- or two-piece stainless steel.

Disc:  Aluminum bronze.

200 CWP, Iron, Single-Flange Butterfly Valves with NBR Seat and Aluminum-Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-367AB, or a comparable product by one of the following:

Description:

Standard:  MSS SP-67, Type I.

CWP Rating:  200 psig (1380 kPa).

Body Design:  Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

Body Material:  ASTM A 126, cast iron or ASTM A 536, ductile iron.

Seat:  NBR.

Stem:  One- or two-piece stainless steel.

Disc:  Aluminum bronze.

200 CWP, Ductile Iron, Single-Flange Butterfly Valves with EPDM Seat and Ductile-Iron Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-365DI, or a comparable product by one of the following:

Description:

Standard:  MSS SP-67, Type I.

CWP Rating:  200 psig (1380 kPa).

Body Design:  Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

Body Material:  ASTM A 536, ductile iron.

Seat:  EPDM.

Stem:  One- or two-piece stainless steel.

Disc:  Nickel-plated[ or -coated] ductile iron.

200 CWP, Ductile Iron, Single-Flange Butterfly Valves with BUNA-N Seat and Ductile-Iron Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-367DI, or a comparable product by one of the following:

Description:

Standard:  MSS SP-67, Type I.

CWP Rating:  200 psig (1380 kPa).

Body Design:  Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

Body Material:  ASTM A 536, ductile iron.

Seat:  BUNA-N.

Stem:  One- or two-piece stainless steel.

Disc:  Nickel-plated[ or -coated] ductile iron.

200 CWP, Ductile Iron, Single-Flange Butterfly Valves with EPDM Seat and Stainless-Steel Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-365SS, or a comparable product by one of the following:

Description:

Standard:  MSS SP-67, Type I.

CWP Rating:  200 psig (1380 kPa).

Body Design:  Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

Body Material:  ASTM A 536, ductile iron.

Seat:  EPDM.

Stem:  One- or two-piece stainless steel.

Disc:  Stainless steel.

200 CWP, Iron, Single-Flange Butterfly Valves with BUNA-N Seat and Stainless-Steel Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-367SS, or a comparable product by one of the following:

Description:

Standard:  MSS SP-67, Type I.

CWP Rating:  200 psig (1380 kPa).

Body Design:  Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

Body Material:  ASTM A 536, ductile iron.

Seat:  BUNA-N.

Stem:  One- or two-piece stainless steel.

Disc:  Stainless steel.

DUCTILE IRON, WAFER BUTTERFLY VALVES

Retain one or more of six paragraphs in this article if ductile iron, wafer butterfly valves are required.  MSS SP-72 covers wafer butterfly valves NPS 1/2 to NPS 36 (DN 15 to DN 900).

200 CWP, Ductile Iron, Wafer Butterfly Valves with EPDM Seat and Aluminum-Bronze Disc:

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-335AB or a comparable product by one of the following:

Description:

Standard:  MSS SP-67, Type I.

CWP Rating:  200 psig (1380 kPa).

Body Design:  Wafer type.

Body Material:  ASTM A 536, ductile iron.

Seat:  EPDM.

Stem:  One- or two-piece stainless steel.

Disc:  Aluminum bronze.

200 CWP,  Ductile Iron, Wafer Butterfly Valves with Buna-N Seat and Aluminum-Bronze Disc:

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-337AB or a comparable product by one of the following:

Description:

Standard:  MSS SP-67, Type I.

CWP Rating:  200 psig (1380 kPa).

Body Design:  Wafer type.

Body Material:  ASTM A 536, ductile iron.

Seat:  Buna-N.

Stem:  One- or two-piece stainless steel.

Disc:  Aluminum bronze.

200 CWP, Ductile Iron, Wafer Butterfly Valves with EPDM Seat and Ductile-Iron Disc:

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-335DI or a comparable product by one of the following:

Description:

Standard:  MSS SP-67, Type I.

CWP Rating:  200 psig (1380 kPa).

Body Design:  Wafer type.

Body Material:  ASTM A 536, ductile iron.

Seat:  EPDM.

Stem:  One- or two-piece stainless steel.

Disc:  Nickel-plated[ or -coated] ductile iron.

200 CWP, Ductile Iron, Wafer Butterfly Valves with Buna-N Seat and Ductile-Iron Disc:

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-337DI or a comparable product by one of the following:

Description:

Standard:  MSS SP-67, Type I.

CWP Rating:  200 psig (1380 kPa).

Body Design:  Wafer type.

Body Material:  ASTM A 536, ductile iron.

Seat:  Buna-N.

Stem:  One- or two-piece stainless steel.

Disc:  Nickel-plated[ or -coated] ductile iron.

200 CWP, Ductile Iron, Wafer Butterfly Valves with EPDM Seat and Stainless-Steel Disc:

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-335SS or a comparable product by one of the following:

Description:

Standard:  MSS SP-67, Type I.

CWP Rating:  200 psig (1380 kPa).

Body Design:  Wafer type.

Body Material:  ASTM A 536, ductile iron.

Seat:  EPDM.

Stem:  One- or two-piece stainless steel.

Disc:  Stainless steel.

200 CWP, Ductile Iron, Wafer Butterfly Valves with Buna-N Seat and Stainless-Steel Disc:

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-337SS or a comparable product by one of the following:

Description:

Standard:  MSS SP-67, Type I.

CWP Rating:  200 psig (1380 kPa).

Body Design:  Wafer type.

Body Material:  ASTM A 536, ductile iron.

Seat:  Buna-N.

Stem:  One- or two-piece stainless steel.

Disc:  Stainless steel.

IRON, GROOVED-END BUTTERFLY VALVES

Retain one or both paragraphs in this article if iron, grooved-end butterfly valves are required.  MSS SP-67 covers iron, grooved-end butterfly valves NPS 1-1/2 to NPS 72 (DN 40 to DN 1800).

Class 150, Bronze Swing Check Valves with Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-453 or a comparable product by one of the following:

Crane Co.; Crane Valve Group; Crane Valves.

Kitz Corporation.

Milwaukee Valve Company.

NIBCO INC.

<Insert manufacturer's name>.

Description:

Standard:  MSS SP-80, Type 3.

CWP Rating:  300 psig (2070 kPa).

Body Design:  Horizontal flow.

Body Material:  ASTM B 62, bronze.

Ends:  Threaded.

Disc:  Bronze.

IRON SWING CHECK VALVES

Retain one or more of three paragraphs in this article if iron swing check valves are required.  MSS SP-71 covers iron swing check valves NPS 2 to NPS 24 (DN 50 to DN 600).

Class 125, Iron Swing Check Valves with Metal Seats:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; Model T-311 or a comparable product by one of the following:

Description:

Standard:  MSS SP-71, Type I.

CWP Rating:  200 psig (1380 kPa).

Body Design:  Clear or full waterway.

Body Material:  ASTM A 126, gray iron with bolted bonnet.

Ends:  Flanged.

Trim:  Bronze.

Gasket:  Asbestos free.

BRONZE GATE VALVES

Retain one or more of four paragraphs in this article if bronze gate valves are required.  MSS SP-80 covers bronze gate valves NPS 1/4 to NPS 3 (DN 8 to DN 80).

Class 125, NRS Bronze Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Legend Valve & Fitting, Inc.; [Model S-415] [Model T-415], or a comparable product by one of the following:

Description:

Standard:  MSS SP-80, Type 1.

CWP Rating:  200 psig (1380 kPa).

Body Material:  ASTM B 62, bronze with integral seat and screw-in bonnet.

Ends:  Threaded[ or solder joint].

Stem:  Bronze.

Disc:  Solid wedge; bronze.

Packing:  Asbestos free.

Handwheel:  Malleable iron[, bronze, or aluminum].